CUSTOMER SERVICE REPORT

| REPORT DATE | 23-06-2026 09:23 | REPORT NO | SRN-5636031 |
| --- | --- | --- | --- |
| COMPANY NAME | INTERNATIONAL INSTITUTE OF BIOTECHNOLOGY & TOXICOLOGY (IIBAT) | CALL TRACKING NUMBER | CC-02127516 |
| SITE PERSON NAME | JAYAVEL | TYPE OF CALL | Commissioning |
| SITE PERSON NUMBER | 9843813380 | FABRICATION NUMBER | BZCK021338 |
| SITE PERSON EMAIL ID | jayavelHVAC@iibat.com | MODEL | AR 0150N A1 |
| SITE LOCATION |  | PRODUCT | EPSAC - ACCESSORIES (EPSAC) |
| SALE DEALER |  | PRE COMMISSIONING DATE |  |
| SERVICE DEALER |  | COMMISSIONING DATE |  |
| AMC STATUS | In AMC | WARRANTY STATUS | Out of Warranty |
| AMC REGISTRATION NO |  | LOAD HMR | 2 |
| AMC TYPE |  | UNLOAD HMR | 0 |
| AMC VISIT NO |  | TOTAL HMR | 2 |

| PARAMETERS | ACTUALS | RESPONSE |  | REPLACED DATE |
| --- | --- | --- | --- | --- |
| Is DSF Available |  | No |  |  |
| Dryer Compressor Serial Number | NT6220Z | Yes |  |  |
| Dryer Compressor Make | NIDEC | Yes |  |  |
| Incoming Cable Type (CU - Copper /AL - Aluminium) | COPPER | Yes |  |  |
| Incoming Cable Size (sq.mm) | 2.5 | Yes |  |  |
| Backup fuse (Amps) | 8 | Yes |  |  |
| Earthing cable size (sq.mm) | 2.5 | Yes |  |  |
| Earth leakage voltage less than 2V AC (Volts) | 0.5 | Yes |  |  |
| Type of refrigerant (refer name plate) | R134a | Yes |  |  |
| Quantity of refrigerant (refer name plate) | 0.60 | Yes |  |  |
| Rated Pressure | 16 | Yes |  |  |
| FAD | 4.02 | Yes |  |  |
| Air inlet temperature (<45 deg C / 113 deg F) | 34 | Yes |  |  |
| Dew point temperature (3~7 deg C / 37.4~44.6 deg F) | 3 | Yes |  |  |
| Discharge pressure (R134a -140 to 200 psi) (R407c -140 to 350 psi) | 180 | Yes |  |  |
| Suction pressure (R134a - 25 to 45 psi) (R407c -45 to 65 psi) | 30 | Yes |  |  |
| Idle pressure (R134a - 100 psi) (R407c -150 psi) | 100 | Yes |  |  |
| Supply voltage (230V / 415 V) | 219 | Yes |  |  |
| Rated current (Amps) | 2.5 | Yes |  |  |
| Is the Operation and Maintenance of compressor explained to customer |  | Yes |  |  |
| Is the OMM and Parts manual handed over to customer |  | Yes |  |  |
| Is the Warranty certificate handed over to customer |  | Yes |  |  |
| NO OF VISITS MADE |  |  |  |  |
| PARTS RECOMMENDED FOR SERVICE |  |  |  |  |
| WORKDONE | Inspected and carried out commissioning. Gas pressure was checked, fan direction was checked, and dew point was checked. All parameters were checked and found within normal limits. |  |  |  |
| PARTS DUE FOR NEXT SERVICE |  |  |  |  |
| Oil Remaining Hours |  |  |  |  |
| Oil Replaced Date |  |  |  |  |
| Type of Oil |  |  |  |  |
| NEXT SERVICE HMR |  | NEXT SERVICE DUE ON |  |  |
| IS THE SERVICE CHARGES APPLICABLE | No | SERVICE CHARGES |  |  |
| ENGINEER | Sharif Ahamed | CONTACT NO |  |  |
| DEALER | ELGi - Chennai |  |  |  |
| CUSTOMER FEEDBACK |  |  |  |  |
| ENGINEER REMARKS | It is recommended to close the open sides of the compressor room to prevent rainwater and direct sunlight exposure, which may affect the performance and reliability of the dryer system. |  |  |  |

| NAME | SIGNATURE |
| --- | --- |